{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["Sheet1","压力表参数"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":5,"n_cols":5,"rows_kept":5,"merged":[[0,0,0,8],[1,0,1,8],[5,0,5,8],[6,0,6,8]],"flags":["formulas_cached_only"]}
["浙江巨化自动化仪表有限公司"]
[]
["序号","位 号","设备名称","型    号","数量"]
[8,null,"热电阻","RT24M PT100 TH02B 铠装芯：∅8 - 防爆等级：ExdIICT4  套管：TH02B  套管/材质∅16*9/304L+PFA 法兰： HG/T 20592 DN40(B) PN40RF U=500mm",5]
[9,null,null,"合计",5]

{"sheet":"压力表参数","index":1,"n_rows":87,"n_cols":12,"rows_kept":87,"merged":[[0,0,2,1],[0,2,2,5],[0,6,0,8],[0,9,0,11],[1,6,1,8],[1,9,1,11],[2,6,2,8],[2,9,2,11],[3,0,3,1],[3,3,3,5],[3,7,3,8],[3,9,3,11],[4,0,6,0],[4,1,4,4],[4,5,6,7],[4,8,6,10],[4,11,6,11],[5,1,6,1],[5,2,6,2],[5,3,6,3],[5,4,6,4],[7,6,7,7],[7,8,7,10],[8,6,8,7],[8,8,8,10],[9,6,9,7],[9,8,9,10],[10,6,10,7],[10,8,10,10],[11,6,11,7],[11,8,11,10],[12,6,12,7],[12,8,12,10],[13,6,13,7],[13,8,13,10],[14,5,14,7],[14,8,14,10],[15,5,15,7],[15,8,15,10],[16,5,16,7],[16,8,16,10],[17,5,17,7],[17,8,17,10],[18,0,18,11],[19,0,19,11],[20,0,20,3],[20,4,20,11],[21,0,21,3],[21,4,21,11],[22,0,22,3],[22,4,22,11],[23,0,23,3],[23,4,23,11],[24,0,24,3],[24,4,24,11],[25,0,25,3],[25,4,25,11],[26,0,26,3],[26,4,26,11],[27,0,27,3],[27,4,27,11],[28,0,28,3],[28,4,28,11],[29,0,29,3],[29,4,29,11],[30,0,30,3],[30,4,30,11],[31,0,31,3],[31,4,31,11],[32,0,32,3],[32,4,32,11],[33,0,33,3],[33,4,33,11],[34,0,34,3],[34,4,34,11],[35,0,35,3],[35,4,35,11],[36,0,36,3],[36,4,36,11],[37,0,38,11],[39,4,39,5],[39,6,39,7],[39,8,39,10],[40,6,40,7],[40,8,40,10],[41,4,41,5],[41,6,41,7],[41,8,41,10],[42,0,43,0],[42,1,43,1],[42,2,43,2],[42,3,43,3],[42,4,43,5],[42,6,43,7],[42,8,43,10],[42,11,43,11],[44,0,46,1],[44,2,46,5],[44,6,44,8],[44,9,44,11],[45,6,45,8],[45,9,45,11],[46,6,46,8],[46,9,46,11],[47,0,47,1],[47,3,47,5],[47,7,47,8],[47,9,47,11],[48,0,50,0],[48,1,48,4],[48,5,50,7],[48,8,50,10],[48,11,50,11],[49,1,50,1],[49,2,50,2],[49,3,50,3],[49,4,50,4],[51,6,51,7],[51,8,51,10],[52,6,52,7],[52,8,52,10],[53,6,53,7],[53,8,53,10],[54,6,54,7],[54,8,54,10],[55,6,55,7],[55,8,55,10],[56,6,56,7],[56,8,56,10],[57,6,57,7],[57,8,57,10],[58,5,58,7],[58,8,58,10],[59,5,59,7],[59,8,59,10],[60,5,60,7],[60,8,60,10],[61,5,61,7],[61,8,61,10],[62,0,62,11],[63,0,63,11],[64,0,64,3],[64,4,64,11],[65,0,65,3],[65,4,65,11],[66,0,66,3],[66,4,66,11],[67,0,67,3],[67,4,67,11],[68,0,68,3],[68,4,68,11],[69,0,69,3],[69,4,69,11],[70,0,70,3],[70,4,70,11],[71,0,71,3],[71,4,71,11],[72,0,72,3],[72,4,72,11],[73,0,73,3],[73,4,73,11],[74,0,74,3],[74,4,74,11],[75,0,75,3],[75,4,75,11],[76,0,76,3],[76,4,76,11],[77,0,77,3],[77,4,77,11],[78,0,78,3],[78,4,78,11],[79,0,79,3],[79,4,79,11],[80,0,80,3],[80,4,80,11],[81,0,82,11],[83,4,83,5],[83,6,83,7],[83,8,83,10],[84,6,84,7],[84,8,84,10],[85,4,85,5],[85,6,85,7],[85,8,85,10],[86,0,87,0],[86,1,87,1],[86,2,87,2],[86,3,87,3],[86,4,87,5],[86,6,87,7],[86,8,87,10],[86,11,87,11]],"flags":["formulas_cached_only"]}
["浙江衢化氟化学有限公司                 ",null,"仪表数据表                                   隔膜压力表                        ",{"$nulls":3},"工程名称"]
[{"$nulls":6},"设计项目"]
[{"$nulls":6},"图号"]
["用户",null,"合同号",{"$nulls":3},"设计阶段","施工图",null,"第    页     共    页"]
["位号","操作条件",{"$nulls":3},"刻度范围 MPa",null,null,"P&ID  号 ",null,null,"安装位置"]
[null,"工艺介质","温度℃","压力MPaG","最大压力MPaG"]
[]
["3PG-402J-1","R32",40,"-0.1/2.7",null,"0~0.7","-0.1~5.9"]
["3PG-431-1","R32",38,"-0.1/3.4",null,"0~0.7","-0.1~5.9"]
["3PG-431-2","R32",38,"-0.1/3.4",null,"0~0.7","-0.1~5.9"]
["3PG-402I-1","R32",40,"-0.1/3.4",null,"0~0.7","-0.1~5.9"]
["3PG-402I-2","R32",40,"-0.1/3.4",null,"0~0.7","-0.1~5.9"]
["3PG-431A","R32",40,3.1,null,"0~0.7","0~6.0"]
["3PG-431B","R32",40,3.1,null,"0~0.7","0~6.0"]
[]
[]
[]
[]
[]
["压力表规格"]
["型号",{"$nulls":3},"隔膜耐震压力表"]
["测量元件形式"]
["测量元件材质",{"$nulls":3},"316L"]
["表壳公称直径 mm",{"$nulls":3},"φ100"]
["精度",{"$nulls":3},1.6]
["隔膜材质",{"$nulls":3},"HC"]
["表壳材质",{"$nulls":3},304]
["防护等级",{"$nulls":3},"IP65"]
["工艺连接体材质",{"$nulls":3},304]
["填充介质",{"$nulls":3},"硅油"]
["工艺连接形式",{"$nulls":3},"法兰"]
["螺纹规格"]
["法兰标准及尺寸",{"$nulls":3},"HG/T20592 DN25(B)-PN63 M"]
["毛细管长度"]
["安装图号"]
[]
["制造厂"]
["供货周期八周内"]
[]
[]
[]
[]
["版次","说明","设计","日期","校核",null,"日期",null,"审核",null,null,"日期"]
[]
["浙江衢化氟化学有限公司                 ",null,"仪表数据表                                   隔膜压力表                        ",{"$nulls":3},"工程名称"]
[{"$nulls":6},"设计项目"]
[{"$nulls":6},"图号"]
["用户",null,"合同号",{"$nulls":3},"设计阶段","施工图",null,"第    页     共    页"]
["位号","操作条件",{"$nulls":3},"刻度范围 MPa",null,null,"P&ID  号 ",null,null,"安装位置"]
[null,"工艺介质","温度℃","压力MPaG","最大压力MPaG"]
[]
["3PG-431","循环水",32,0.5,null,"0~0.7","0~1.0"]
["3PG-432","过热蒸汽",180,0.5,null,null,"0~1.0",{"$nulls":4},"带冷凝圈"]
{"$rows_empty":10}
["压力表规格"]
["型号",{"$nulls":3},"耐震压力表"]
["测量元件形式"]
["测量元件材质",{"$nulls":3},"316L"]
["表壳公称直径 mm",{"$nulls":3},"φ100"]
["精度",{"$nulls":3},1.6]
["隔膜材质"]
["表壳材质",{"$nulls":3},304]
["防护等级",{"$nulls":3},"IP65"]
["工艺连接体材质",{"$nulls":3},304]
["填充介质"]
["工艺连接形式",{"$nulls":3},"螺纹"]
["螺纹规格",{"$nulls":3},"M20×1.5"]
["法兰标准及尺寸"]
["毛细管长度"]
["安装图号"]
[{"$nulls":4},"带引压法兰及焊接好的活套接头"]
["制造厂"]
["供货周期八周内"]
[]
[]
[]
[]
["版次","说明","设计","日期","校核",null,"日期",null,"审核",null,null,"日期"]