{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet3","涡街流量计","电接点液位计 "],"not_rendered":{"images":5,"external_links":1,"defined_names":3},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet3","index":0,"n_rows":0,"n_cols":0,"rows_kept":0,"hidden":true,"flags":["formulas_cached_only"]}

{"sheet":"涡街流量计","index":1,"n_rows":94,"n_cols":11,"rows_kept":94,"merged":[[0,0,1,2],[0,3,1,7],[0,8,0,9],[1,8,1,9],[2,0,2,2],[2,3,2,7],[2,8,2,9],[3,0,3,7],[3,8,3,9],[4,2,4,4],[4,5,4,7],[4,8,4,10],[5,0,6,0],[5,2,5,4],[5,5,5,7],[5,8,5,10],[6,2,6,4],[6,5,6,7],[6,8,6,10],[7,2,7,4],[7,5,7,7],[7,8,7,10],[8,2,8,4],[8,5,8,7],[8,8,8,10],[9,2,9,4],[9,5,9,7],[9,8,9,10],[10,2,10,4],[10,5,10,7],[10,8,10,10],[11,0,11,10],[12,2,12,4],[12,5,12,7],[12,8,12,10],[13,2,13,4],[13,5,13,7],[13,8,13,10],[14,2,14,4],[14,5,14,7],[14,8,14,10],[15,0,15,1],[15,2,15,4],[15,5,15,7],[15,8,15,10],[16,0,16,1],[16,2,16,4],[16,5,16,7],[16,8,16,10],[17,0,17,1],[17,2,17,4],[17,5,17,7],[17,8,17,10],[18,2,18,4],[18,5,18,7],[18,8,18,10],[19,0,19,10],[20,0,20,1],[20,2,20,4],[20,5,20,7],[20,8,20,10],[21,0,21,1],[21,2,21,4],[21,5,21,7],[21,8,21,10],[22,0,22,1],[22,2,22,4],[22,5,22,7],[22,8,22,10],[23,0,23,1],[23,2,23,4],[23,5,23,7],[23,8,23,10],[24,0,24,1],[24,2,24,4],[24,5,24,7],[24,8,24,10],[25,0,25,1],[25,2,25,4],[25,5,25,7],[25,8,25,10],[26,0,26,1],[26,2,26,4],[26,5,26,7],[26,8,26,10],[27,0,27,1],[27,2,27,4],[27,5,27,7],[27,8,27,10],[28,0,28,1],[28,2,28,4],[28,5,28,7],[28,8,28,10],[29,0,29,1],[29,2,29,4],[29,5,29,7],[29,8,29,10],[30,0,30,1],[30,2,30,4],[30,5,30,7],[30,8,30,10],[31,0,31,10],[32,0,32,1],[32,2,32,4],[32,5,32,7],[32,8,32,10],[33,0,33,1],[33,2,33,4],[33,5,33,7],[33,8,33,10],[34,0,34,1],[34,2,34,4],[34,5,34,7],[34,8,34,10],[35,0,35,1],[35,2,35,4],[35,5,35,7],[35,8,35,10],[36,0,36,1],[36,2,36,4],[36,5,36,7],[36,8,36,10],[37,0,37,1],[37,2,37,4],[37,5,37,7],[37,8,37,10],[38,0,38,1],[38,2,38,4],[38,5,38,7],[38,8,38,10],[39,0,39,1],[39,2,39,4],[39,5,39,7],[39,8,39,10],[40,0,40,1],[40,2,40,4],[40,5,40,7],[40,8,40,10],[41,0,41,1],[41,2,41,4],[41,5,41,7],[41,8,41,10],[42,0,42,1],[42,2,42,4],[42,5,42,7],[42,8,42,10],[43,0,43,1],[43,2,43,4],[43,5,43,7],[43,8,43,10],[44,0,44,1],[44,2,44,10],[45,0,45,1],[45,2,45,4],[45,5,45,7],[45,8,45,10],[46,0,46,1],[46,2,47,4],[46,5,47,7],[46,8,47,10],[47,0,47,1],[48,0,48,10],[49,2,49,4],[49,5,49,7],[49,8,49,10],[50,0,51,0],[50,2,50,4],[50,5,50,7],[50,8,50,10],[51,2,51,4],[51,5,51,7],[51,8,51,10],[52,2,52,4],[52,5,52,7],[52,8,52,10],[53,2,53,4],[53,5,53,7],[53,8,53,10],[54,2,54,4],[54,5,54,7],[54,8,54,10],[55,2,55,4],[55,5,55,7],[55,8,55,10],[56,0,56,10],[57,2,57,4],[57,5,57,7],[57,8,57,10],[58,2,58,4],[58,5,58,7],[58,8,58,10],[59,2,59,4],[59,5,59,7],[59,8,59,10],[60,0,60,1],[60,2,60,4],[60,5,60,7],[60,8,60,10],[61,0,61,1],[61,2,61,4],[61,5,61,7],[61,8,61,10],[62,0,62,1],[62,2,62,4],[62,5,62,7],[62,8,62,10],[63,2,63,4],[63,5,63,7],[63,8,63,10],[64,0,64,10],[65,0,65,1],[65,2,65,4],[65,5,65,7],[65,8,65,10],[66,0,66,1],[66,2,66,4],[66,5,66,7],[66,8,66,10],[67,0,67,1],[67,2,67,4],[67,5,67,7],[67,8,67,10],[68,0,68,1],[68,2,68,4],[68,5,68,7],[68,8,68,10],[69,0,69,1],[69,2,69,4],[69,5,69,7],[69,8,69,10],[70,0,70,1],[70,2,70,4],[70,5,70,7],[70,8,70,10],[71,0,71,1],[71,2,71,4],[71,5,71,7],[71,8,71,10],[72,0,72,1],[72,2,72,4],[72,5,72,7],[72,8,72,10],[73,0,73,1],[73,2,73,4],[73,5,73,7],[73,8,73,10],[74,0,74,1],[74,2,74,4],[74,5,74,7],[74,8,74,10],[75,0,75,1],[75,2,75,4],[75,5,75,7],[75,8,75,10],[76,0,76,10],[77,0,77,1],[77,2,77,4],[77,5,77,7],[77,8,77,10],[78,0,78,1],[78,2,78,4],[78,5,78,7],[78,8,78,10],[79,0,79,1],[79,2,79,4],[79,5,79,7],[79,8,79,10],[80,0,80,1],[80,2,80,4],[80,5,80,7],[80,8,80,10],[81,0,81,1],[81,2,81,4],[81,5,81,7],[81,8,81,10],[82,0,82,1],[82,2,82,4],[82,5,82,7],[82,8,82,10],[83,0,83,1],[83,2,83,4],[83,5,83,7],[83,8,83,10],[84,0,84,1],[84,2,84,4],[84,5,84,7],[84,8,84,10],[85,0,85,1],[85,2,85,4],[85,5,85,7],[85,8,85,10],[86,0,86,1],[86,2,86,4],[86,5,86,7],[86,8,86,10],[87,0,87,1],[87,2,87,4],[87,5,87,7],[87,8,87,10],[88,0,88,1],[88,2,88,4],[88,5,88,7],[88,8,88,10],[89,0,89,1],[89,2,89,10],[90,0,90,1],[90,2,90,4],[90,5,90,7],[90,8,90,10],[91,0,91,1],[91,2,92,4],[91,5,91,7],[91,8,91,10],[92,0,92,1],[92,5,92,7],[92,8,92,10],[93,0,93,10]],"flags":["formulas_cached_only"]}
[" ",null,null,"100KTA聚偏二氯乙烯高性能阻隔材料项目（二期B段）尾气处理装置工艺包设计\n+整套设备采购",{"$nulls":4},"设计阶段",null,"施工图"]
[{"$nulls":8},"图 号",null,"TLJ23026-K0301-05"]
["仪表数据表",null,null,"孔板流量计",{"$nulls":4},"日 期",null,"2025-11-08"]
["  审  核:                        校  核:                         设   计:                              会   签： ",{"$nulls":7},"版 次",null,"第一版"]
["位号",null,"FIQ-292109",null,null,"FIQ-292110",null,null,"FIQ-292111"]
["用途 ",null,"氮气1",null,null,"氮气2",null,null,"氮气3"]
[null,null,"孔板流量计",null,null,"孔板流量计",null,null,"孔板流量计"]
["P＆ID 号"]
["管道编号/设备编号",null,"N-0105-25-M1E",null,null,"N-0106-25-M1E",null,null,"N-0107-15-M1E"]
["管道材质",null,"M1E",null,null,"M1E",null,null,"M1E"]
["管道规格",null,"DN25",null,null,"DN25",null,null,"DN15"]
["操作条件"]
["工艺介质",null,"氮气",null,null,"氮气",null,null,"氮气"]
["操作压力  ","MPa（G）","0.3~0.5",null,null,"0.3~0.5",null,null,"0.3~0.5"]
["操作温度   "," ℃","常温",null,null,"常温",null,null,"常温"]
["最大流量",null,"100Nm3/h",null,null,"100Nm3/h",null,null,"50Nm3/h"]
["正常流量",null,"50Nm3/h",null,null,"50Nm3/h",null,null,"30Nm3/h"]
["最小流量",null,"0Nm3/h",null,null,"0Nm3/h",null,null,"0Nm3/h"]
["操作密度","kg/m3 ",1.25,null,null,1.25,null,null,1.25]
["传感器规格"]
["类型"]
["结构形式",null,"法兰式",null,null,"法兰式",null,null,"法兰式"]
["测量形式",null,"孔板流量（配差压变送器）",null,null,"孔板流量（配差压变送器）",null,null,"孔板流量（配差压变送器）"]
["仪表量程",null,"120Nm3/h",null,null,"120Nm3/h",null,null,"60Nm3/h"]
["防爆等级",null,"不低于Exd IIC T4隔爆型",null,null,"不低于Exd IIC T4隔爆型",null,null,"不低于Exd IIC T4隔爆型"]
["防护等级",null,"IP67",null,null,"IP67",null,null,"IP67"]
["本体材质",null,"碳钢",null,null,"碳钢",null,null,"碳钢"]
["衬里材质"]
["法兰尺寸",null,"DN25",null,null,"DN25",null,null,"DN15"]
["法兰标准及等级",null,"焊颈法兰，PN40,RF,\nHG20592-09",null,null,"焊颈法兰，PN40,RF,\nHG20592-09",null,null,"焊颈法兰，PN40,RF,\nHG20592-09"]
["接地环材质"]
["变送器规格"]
["型号"]
["变送器类型",null,"分体式",null,null,"分体式",null,null,"分体式"]
["变送器材质",null,"铸铝",null,null,"铸铝",null,null,"铸铝"]
["电源",null,"24VDC",null,null,"24VDC",null,null,"24VDC"]
["精度",null,"±0.5%FS",null,null,"±0.5%FS",null,null,"±0.5%FS"]
["输出信号",null,"二线制4-20mA+HART",null,null,"二线制4-20mA+HART",null,null,"二线制4-20mA+HART"]
["电气接口尺寸",null,"M20×1.5（内）",null,null,"M20×1.5（内）",null,null,"M20×1.5（内）"]
["电缆长度",null,"/",null,null,"/",null,null,"/"]
["防爆等级",null,"不低于Exd IIC T4隔爆型",null,null,"不低于Exd IIC T4隔爆型",null,null,"不低于Exd IIC T4隔爆型"]
["防护等级",null,"IP67",null,null,"IP67",null,null,"IP67"]
["安装形式",null,"/",null,null,"/",null,null,"/"]
["输出指示表",null,"LCD",null,null,"LCD",null,null,"LCD"]
["制造厂",null,"艾默生/横河/E+H"]
["数量",null,"1套",null,null,"1套",null,null,"1套"]
["备注",null,"配引压管，带防水防爆接头",null,null,"配引压管，带防水防爆接头",null,null,"配引压管，带防水防爆接头"]
["注释："]
["说明：流量计采购时需要厂家提供特种设备制造许可证以及特种设备监督检验证书"]
["位号",null,"FIQ-292112"]
["用途 ",null,"氮气4"]
[null,null,"孔板流量计"]
["P＆ID 号"]
["管道编号/设备编号",null,"N-0108-25-M1E"]
["管道材质",null,"M1E"]
["管道规格",null,"DN25"]
["操作条件"]
["工艺介质",null,"氮气"]
["操作压力  ","MPa（G）","0.3~0.5"]
["操作温度   "," ℃","常温"]
["最大流量 高报",null,"100Nm3/h"]
["正常流量",null,"50Nm3/h"]
["最小流量 低报",null,"0Nm3/h"]
["操作密度","kg/m3 ",1.25]
["传感器规格"]
["类型"]
["结构形式",null,"法兰式"]
["测量形式",null,"孔板流量（配差压变送器）"]
["仪表量程",null,"130Nm3/h"]
["防爆等级",null,"不低于Exd IIC T4隔爆型"]
["防护等级",null,"IP67"]
["本体材质",null,"碳钢"]
["衬里材质"]
["法兰尺寸",null,"DN25"]
["法兰标准及等级",null,"焊颈法兰，PN40,RF,\nHG20592-09"]
["接地环材质"]
["变送器规格"]
["型号"]
["变送器类型",null,"分体式"]
["变送器材质",null,"铸铝"]
["电源",null,"24VDC"]
["精度",null,"±0.5%FS"]
["输出信号",null,"二线制4-20mA+HART"]
["电气接口尺寸",null,"M20×1.5（内）"]
["电缆长度",null,"/"]
["防爆等级",null,"本安防爆ExiaIICT4"]
["防护等级",null,"IP67"]
["安装形式",null,"/"]
["输出指示表",null,"LCD"]
["制造厂",null,"艾默生/横河/E+H"]
["数量",null,"1套"]
["备注",null,"配引压管，带防水防爆接头"]
["注释："]
["说明：流量计采购时需要厂家提供特种设备制造许可证以及特种设备监督检验证书"]

{"sheet":"电接点液位计 ","index":2,"n_rows":47,"n_cols":11,"rows_kept":47,"merged":[[0,0,1,2],[0,3,1,7],[0,8,0,9],[1,8,1,9],[2,0,2,2],[2,3,2,7],[2,8,2,9],[3,0,3,7],[3,8,3,9],[4,2,4,4],[4,5,4,7],[4,8,4,10],[5,2,5,4],[5,5,5,7],[5,8,5,10],[6,2,6,4],[6,5,6,7],[6,8,6,10],[7,2,7,4],[7,5,7,7],[7,8,7,10],[8,2,8,4],[8,5,8,7],[8,8,8,10],[9,0,9,10],[10,2,10,4],[10,5,10,7],[10,8,10,10],[11,2,11,4],[11,5,11,7],[11,8,11,10],[12,2,12,4],[12,5,12,7],[12,8,12,10],[13,2,13,4],[13,5,13,7],[13,8,13,10],[14,2,14,4],[14,5,14,7],[14,8,14,10],[15,0,15,10],[16,2,16,4],[16,5,16,7],[16,8,16,10],[17,2,17,4],[17,5,17,7],[17,8,17,10],[18,0,18,1],[18,2,18,4],[18,5,18,7],[18,8,18,10],[19,2,19,4],[19,5,19,7],[19,8,19,10],[20,2,20,4],[20,5,20,7],[20,8,20,10],[21,2,21,4],[21,5,21,7],[21,8,21,10],[22,2,22,4],[22,5,22,7],[22,8,22,10],[23,2,23,4],[23,5,23,7],[23,8,23,10],[24,2,24,4],[24,5,24,7],[24,8,24,10],[25,2,25,4],[25,5,25,7],[25,8,25,10],[26,2,26,4],[26,5,26,7],[26,8,26,10],[27,2,27,4],[27,5,27,7],[27,8,27,10],[28,2,28,4],[28,5,28,7],[28,8,28,10],[29,2,29,4],[29,5,29,7],[29,8,29,10],[30,2,30,4],[30,5,30,7],[30,8,30,10],[31,2,31,4],[31,5,31,7],[31,8,31,10],[32,2,32,4],[32,5,32,7],[32,8,32,10],[33,0,33,10],[34,0,34,1],[34,2,34,4],[34,5,34,7],[34,8,34,10],[35,0,35,1],[35,2,35,4],[35,5,35,7],[35,8,35,10],[36,0,36,1],[36,2,36,4],[36,5,36,7],[36,8,36,10],[37,2,37,4],[37,5,37,7],[37,8,37,10],[38,0,38,1],[38,2,38,4],[38,5,38,7],[38,8,38,10],[39,0,39,1],[39,2,39,4],[39,5,39,7],[39,8,39,10],[40,0,40,1],[40,2,40,4],[40,5,40,7],[40,8,40,10],[41,0,41,1],[41,2,41,4],[41,5,41,7],[41,8,41,10],[42,0,42,1],[42,2,42,4],[42,5,42,7],[42,8,42,10],[43,0,43,1],[43,2,43,4],[43,5,43,7],[43,8,43,10],[44,2,44,10],[45,2,45,4],[45,5,45,7],[45,8,45,10],[46,2,46,4],[46,5,46,7],[46,8,46,10]],"flags":["formulas_cached_only"]}
[" ",null,null,"100KTA聚偏二氯乙烯高性能阻隔材料项目（二期B段）尾气处理装置工艺包设计\n+整套设备采购",{"$nulls":4},"设计阶段",null,"施工图"]
[{"$nulls":8},"图 号",null,"TLJ23026-K0301-08"]
["仪表数据表",null,null,"电接点液位计 ",{"$nulls":4},"日 期",null,"2025-11-08"]
["   审 核:                           校 核:                                设 计:                                会 签：  ",{"$nulls":7},"版 次",null,"第 1 版"]
["位号",null,"LS292204"]
["用途 ",null,"锅筒电接点液位计 "]
["P＆ID 号"]
["管道编号/设备编号"]
["箱罐材质"]
["操作条件"]
["工艺介质",null,"饱和蒸汽及水"]
["介质密度","kg/m3",4.515]
["操作压力  ","MPaG",0.8]
["操作温度   "," ℃",175]
["正常料位   ","mm（G）"]
["电接点液位计测量筒规格"]
["型号"]
["测量范围",null,"待定"]
["磁翻板液位计法兰面中心距",null,"440mm"]
["测量点数",null,"15点"]
["电极密封形式",null,"旋入式电极"]
["上限报警设定值",null,"320mm"]
["下限报警设定值",null,"170mm"]
["设计形式",null,"普通型侧装式"]
["电气接口尺寸",null,"M20×1.5，带防水接头"]
["防爆等级",null,"不低于Exd IIC T4隔爆型"]
["防护等级",null,"IP67"]
["安装形式",null,"法兰式"]
["法兰标准及等级",null,"HG20592-09,PN16"]
["法兰尺寸及密封面",null,"DN25,RF"]
["法兰材质",null,"碳钢"]
["附件",null,"带排气及排污阀"]
["数量",null,"1套"]
["二次仪表规格"]
["二次仪表结构",null,"盘装仪表"]
["显示",null,"带LCD显示"]
["电源",null,"AC 220V"]
["输出信号",null,"DC4-20mA+开关量报警"]
["防爆认证",null,"/"]
["电气接口尺寸",null,"M20×1.5"]
["配套电缆长度",null,"10米"]
["防爆等级",null,"不低于Exd IIC T4隔爆型"]
["防护等级",null,"IP67"]
["输出指示表",null,"LCD"]
["制造厂"]
["备注",null,"带防爆防水电气接头，\n带二次仪表防爆安装箱（ExdIICT4）"]
["注释："]